## BacEye-FSL-CONTROL-III_EDE
#Engineering-Data-Exchange
PROJECT_NAME | Standard Project
VERSION_OF_REFERENCEFILE | 1
TIMESTAMP_OF_LAST_CHANGE | 2020-09-14
AUTHOR_OF_LAST_CHANGE
VERSION_OF_LAYOUT | 2
#mandatory | mandatory | mandatory | mandatory | mandatory | optional | optional | optional | optional | optional | optional | optional | optional
# keyname | device obj.-instance | object-name | object-type | object-instance | description | min-present-value | max-present-value | commandable | hi-limit | low-limit | state-text-reference | unit-code
Device(333) | 333 | TROXBOX | 8 | 333
AnalogInput(0) | 333 | fOutFanLevel | 0 | 0 | Act fan level |  |  | N | 100 | 0 |  | 95
AnalogInput(1) | 333 | fOutOperatingState | 0 | 1 | Act operating state |  |  | N | 100 | 0 |  | 95
AnalogInput(2) | 333 | fOutOperatingTypeOverriding | 0 | 2 | Act operating type overriding |  |  | N | 100 | 0 |  | 95
AnalogInput(3) | 333 | fOutValvePositionCoolingSlave03 | 0 | 3 | Act valve pos cooling slave03 |  |  | N | 100 | 0 |  | 98
AnalogInput(4) | 333 | fOutValvePositionHeatingSlave03 | 0 | 4 | Act valve pos heating slave03 |  |  | N | 100 | 0 |  | 98
AnalogInput(5) | 333 | fOutTempSupplySlave03 | 0 | 5 | Act temp supply slave03 |  |  | N | 110 | -50 |  | 62
AnalogInput(6) | 333 | fOutTempSupplySlave02 | 0 | 6 | Act temp supply slave02 |  |  | N | 110 | -50 |  | 62
AnalogInput(7) | 333 | fOutValvePositionHeatingSlave02 | 0 | 7 | Act valve pos heating slave02 |  |  | N | 100 | 0 |  | 98
AnalogInput(8) | 333 | fOutValvePositionCoolingSlave02 | 0 | 8 | Act valve pos cooling slave02 |  |  | N | 100 | 0 |  | 98
AnalogInput(9) | 333 | fOutValvePositionCoolingSlave01 | 0 | 9 | Act valve pos cooling slave01 |  |  | N | 100 | 0 |  | 98
AnalogInput(10) | 333 | fOutValvePositionHeatingSlave01 | 0 | 10 | Act valve pos heating slave01 |  |  | N | 100 | 0 |  | 98
AnalogInput(11) | 333 | fOutTempSupplySlave01 | 0 | 11 | Act temp supply slave01 |  |  | N | 110 | -50 |  | 62
AnalogInput(12) | 333 | fOutAlarmB | 0 | 12 | Act alarm B |  |  | N | 65535 | 0 |  | 95
AnalogInput(13) | 333 | fOutAlarmA | 0 | 13 | Act alarm A |  |  | N | 65535 | 0 |  | 95
AnalogInput(14) | 333 | fOutValvePositionCoolingMaster | 0 | 14 | Act valve pos cooling Master |  |  | N | 100 | 0 |  | 98
AnalogInput(15) | 333 | fOutValvePositionHeatingMaster | 0 | 15 | Act valve pos heating Master |  |  | N | 100 | 0 |  | 98
AnalogInput(16) | 333 | fOutSystemDevices | 0 | 16 | Act system devices |  |  | N | 100 | 0 |  | 95
AnalogInput(17) | 333 | fOutVolumeFlowExhaust | 0 | 17 | Act volume flow exhaust |  |  | N | 10000 | 0 |  | 87
AnalogInput(18) | 333 | fOutVolumeFlowOda | 0 | 18 | Act volume flow Oda |  |  | N | 10000 | 0 |  | 87
AnalogInput(19) | 333 | fOutAirQualityRoom | 0 | 19 | Act air quality room |  |  | N | 10000 | 0 |  | 96
AnalogInput(20) | 333 | fOutAirHumidityRoom | 0 | 20 | Act air humidity room |  |  | N | 100 | 0 |  | 98
AnalogInput(21) | 333 | fOutTempSetPointSupply | 0 | 21 | Act temp set point supply |  |  | N | 110 | -50 |  | 62
AnalogInput(22) | 333 | fOutTempRangeHeating | 0 | 22 | Act temp range heating |  |  | N | 110 | -50 |  | 62
AnalogInput(23) | 333 | fOutTempRangeCooling | 0 | 23 | Act temp range cooling |  |  | N | 110 | -50 |  | 62
AnalogInput(24) | 333 | fOutTempOffset | 0 | 24 | Act temp offset |  |  | N | 110 | -50 |  | 62
AnalogInput(25) | 333 | fOutTempFlow | 0 | 25 | Act temp flow |  |  | N | 110 | -50 |  | 62
AnalogInput(26) | 333 | fOutTempReturnFlow | 0 | 26 | Act temp return flow |  |  | N | 110 | -50 |  | 62
AnalogInput(27) | 333 | fOutTempRoom | 0 | 27 | Act temp room |  |  | N | 110 | -50 |  | 62
AnalogInput(28) | 333 | fOutTempOda | 0 | 28 | Act temp oda |  |  | N | 110 | -50 |  | 62
AnalogInput(29) | 333 | fOutTempSupply | 0 | 29 | Act temp supply |  |  | N | 110 | -50 |  | 62
AnalogValue(0) | 333 | fInSpTempRangeCooling | 2 | 0 | Temp range cooling |  |  | Y | 110 | -50 |  | 62
AnalogValue(1) | 333 | fInSpTempRangeHeating | 2 | 1 | Temp range heating |  |  | Y | 110 | -50 |  | 62
AnalogValue(2) | 333 | fInPvTempRoom | 2 | 2 | Present temp room |  |  | Y | 110 | -50 |  | 62
AnalogValue(3) | 333 | fInSPTempRoom | 2 | 3 | Set point temp room |  |  | Y | 110 | -50 |  | 62
AnalogValue(4) | 333 | fInSpTempOffsetRoom | 2 | 4 | Setpoint temp offset room |  |  | Y | 110 | -50 |  | 62
AnalogValue(5) | 333 | fInSpTempSupply | 2 | 5 | Setpoint temp supply |  |  | Y | 110 | -50 |  | 62
AnalogValue(6) | 333 | fInSpOffsetSupply | 2 | 6 | Setpoint offset supply |  |  | Y | 110 | -50 |  | 62
AnalogValue(7) | 333 | fInPvHumidityRoom | 2 | 7 | Present humidity room |  |  | Y | 100 | 0 |  | 98
AnalogValue(8) | 333 | fInSpFanLevel | 2 | 8 | Setpoint fanlevel |  |  | Y | 100 | 0 |  | 95
AnalogValue(9) | 333 | fInPvAirQualityRoom | 2 | 9 | Present air quality room |  |  | Y | 10000 | 0 |  | 96
AnalogValue(10) | 333 | fInPvAirQualityOda | 2 | 10 | Present air quality oda |  |  | Y | 10000 | 0 |  | 96
AnalogValue(11) | 333 | fInPvVolumeFlowDifference | 2 | 11 | Present volume flow difference |  |  | Y | 10000 | 0 |  | 87
AnalogValue(12) | 333 | fInPvOperatingTypeOverriding | 2 | 12 | Present op type overriding |  |  | Y | 100 | 0 |  | 95
AnalogValue(13) | 333 | fInPvTempOda | 2 | 13 | Present temp oda |  |  | Y | 110 | -50 |  | 62
BinaryValue(0) | 333 | bInFire | 5 | 0 | enable fire |  |  | Y |  |  | 1
BinaryValue(1) | 333 | bInWindow | 5 | 1 | enable window |  |  | Y |  |  | 2
BinaryValue(2) | 333 | bInExtraTime | 5 | 2 | enable extratime |  |  | Y |  |  | 3
BinaryValue(3) | 333 | bInFilterReset | 5 | 3 | enable filter reset |  |  | Y |  |  | 4
BinaryValue(4) | 333 | bInCondensation | 5 | 4 | enable condensation |  |  | Y |  |  | 4
BinaryValue(5) | 333 | bOutFire | 5 | 5 | Current fire |  |  | Y |  |  | 1
BinaryValue(6) | 333 | bOutWindow | 5 | 6 | Current window open |  |  | Y |  |  | 2
BinaryValue(7) | 333 | bOutExtratime | 5 | 7 | Current extratime |  |  | Y |  |  | 5
MultistateInput(0) | 333 | eOutOperatingMode | 13 | 0 | Current Operating mode |  |  | N |  |  | 6
MultistateInput(1) | 333 | eOutOperatingType | 13 | 1 | Current Operating Type |  |  | N |  |  | 7
MultistateInput(2) | 333 | eOutVentilationType | 13 | 2 | Current ventilation type |  |  | N |  |  | 8
MultistateInput(3) | 333 | eOutDemandRoom | 13 | 3 | Current demand room |  |  | N |  |  | 9
MultistateInput(4) | 333 | eOutDemandValve | 13 | 4 | Current demand valve |  |  | N |  |  | 9
MultistateValue(0) | 333 | eInOperatingMode | 19 | 0 | Operating mode |  |  | Y |  |  | 10
MultistateValue(1) | 333 | eInOperatingType | 19 | 1 | Operating mode |  |  | Y |  |  | 11
MultistateValue(2) | 333 | eInChangeOver | 19 | 2 | Change over |  |  | Y |  |  | 12
MultistateValue(3) | 333 | eInCovMode | 19 | 3 | Cov Mode |  |  | Y |  |  | 13
MultistateValue(4) | 333 | eInOdaAutomatic | 19 | 4 | Oda automatic |  |  | Y |  |  | 14